Safety Caution

1. “X” mark following the explosionproof class rating of the positiobers manufactured for power supply type case 2 means that when in operation it is required to observe the following “special” conditions:

· connection of the positioners to the devices installed outside an explosion-hazardous area should be done through ignition-protection barriers which should have the certificate of conformity within certification system of GOST R and application permit from Rostechnadzor for connecting devices located in explosion-hazardous areas inside and outside premises where explosion-hazardous gas mixture of category IIC can  evolve;

· it is prohibited to launch mechanically damaged positioners into operation; 
· input and output intrinsically safe parametres of the positionerswith allowance for the parametres of the connection cable should not exceed electrical parametres mentioned on the safety barrier.
2. When in operation the following application conditions for the positioners made to fit the power supply type case 2 should be observed:
· cable routing in an explosion-hazardous area and protection of cable cords against short circuit or overloads as well as grounding or nulling should comply with the requirements stipulated in clause7.3 ПУЭ and GOST R 51330.13-99 (IEC 60079-14-96);
· connection of external electric circuits should necessarily be done through cable glands, certified within the established order so as to meet the requirements of GOST R 51330.1-99 (IEC 60079-1-98).
