[image: image1.wmf]CARLO GAVAZZI IMPIANTI SpA
CLIENTE / Customer: KHAFJI JONT OPERATIONS

IMPIANTO / Plant: 1.5MMGPD MSF - SEAWATER DESALINATION PLANT
COMMENTS YAMATAKE 

SUBJECT: PRESSURE & DIFFERENTIAL PRESSURE TRANSMITTERS

	1

2

3

4

5

6


	Offer n. Q20051863 YEU-05-780  dated 07/11/05

In the code number  of the each instruments there is indicated the code SH8046, please clarify  I not have found it in yours catalogues.

→The code SH8046 denotes mounting bracket of SUS304 for our internal use. Accordingly, we have deleted

 this code from our proposal.
YAMATAKE has offered the wetted parts in 316 S.S. but are required in 316L S.S please review your offer.

→We must admit that the description of our original proposal was not proper. Accordingly, we now confirm that the materials are as follows.

       Diaphragm(wetted parts): SUS316L,  Cover/Adapter flange: SCS14,  Vent/Drain: SUS316
Please clarify the type of enclosure.
→IEC IP67,  NEMA 3  AND  4X
The instrument WP-PT-721 must be explosion proof. (see the data sheets rev.0)

→Okay, we have changed accordingly.
The instruments WP-FT-322A/B change range. (see the data sheets rev.0)

→Okay, we have changed as follows.

       WP-FT-322B-1, -2 :  Changed to 0-10,000mmH2O

       WP-FT-322A-1, -2 :  Remain unchanged as 0-3810mmH2O.
The instrument WP-DPT-300 has been deleted

→Okay, we have deleted.


SUBJECT: LEVEL TRANSMITTERS

	1

2

3

4


	Offer n. Q20061046 YEU-05-780ADD  dated 09/02/06

Please confirm the type of the enclosure IP-66 (NEMA-4X).

→IP67, NEMA3 AND 4X
Please confirm that the explosion proof instrument are adapts for classified area Class I Zone II.

→Yes, our offered explosion proof instrument has an approval of ATEX EExd IICT6 which is
    same level as Class I Zone II.
Please confirm the accuracy of the instruments (+/-0,1% F.S is required).
→STE929: Accuracy of our instruments are as follows.

     +/_0.3%FS(△P>1250mm H20)   +/_(0.3x12.5/△P)% (△P<1250mmH20)
→STD920: +-0.075% ( for △P>=5000 mm H2O)  +-0.1% (for 5000>△P>= 500mm H2O) +-(0.025 +0.075x5.0/△P)% (for △P<500mm H20)

△P is either URV or LRV or URV-LRV (the greater)

The length of the capillary tube is the same for all 6m.

→Okay, we have changed accordingly.


� EMBED Word.Picture.8  ���








[image: image2.wmf]_1040547008.doc



