[image: image1.wmf][image: image2.emf][image: image3.jpg]




Air Mass Flow Meter (Nitrogen, Compressed Air)
Type: MCF

High Performance at Low Cost
· Excellent Accuracy and Stability
· Distributed cost calculation and consumption control
· Leakage detection
· Alarm functions
Technical Data:
	Basic technical data:

	Model-No.
	MCF0080
	MCF0150
	MCF0151
	MCF025
	MCF040
	MCF050

	Gas type
	Air or N2 (non-condensing, no mist, no dust (0,2 µm)

	Flow rate  range [Nl/min]
	2 – 200
	5 – 500
	10 – 1000
	30 – 3000
	60 – 6000
	120 – 12000

	Reverse flow range [Nl/min]
	-60
	-150
	-300
	-900
	-1800
	-3600

	Extended range [Nl/min]
	400
	1000
	2000
	6000
	12000
	24000

	Accuracy
	±3 % FS

	Accuracy 3%FS range [Nl/min]
	4 – 200
	10 – 500
	20 - 1000
	60 – 3000
	120 – 6000
	240 – 12000

	Display resolution [Nl/min]
	1
	1
	2
	5
	10
	10

	Process connection

	Pipe size
	8A(¼B)Rc
	15A(½B)Rc
	15A(½B)Rc
	25A(1B)Rc
	40A(1½B)Rc
	50A(2B)Rc

	Process connection
	Selectable: G (ISO 228-1), Rc (ISO 7/1), NPT

	Process connection (Europe)
	G ¼”
	G 1/2”
	G 1/2”
	G 1”
	G 1 1/2”
	G 2”

	Material / Weight

	Body material
	Aluminum alloy, with alumite treatment on the surface

	Special treatment
	Selectable: Oil-free treatment, O-Ring FKM fluororubber

	Case material
	Denatured PPO

	Weight
	400 g
	400 g
	400 g
	500 g
	700 g
	1100 g

	Operating conditions

	Operating temperature
	-10 to +60 °C (without condensation)

	Storage temperature
	-20 to +70 ?C (without condensation)

	Humidity
	0 to 90 % RH (without condensation)

	Operating pressure range
	-0.07 to +1.0 MPa (-0,7 bar g to 10 bar g)

	Pressure resistance
	1,5 MPa (15 bar g)

	Mounting orientation
	Horizontal (flow: left → right, right → left)・Vertical (flow: up → down, down → up)

	Power supply / Output signals

	Power supply
	24 VDC, 120 mA max.

	Output signal
	4-20 mA (300 Ω load resistance max.)

	Event output / Pulse  output
	1 Open collector output (rating 30 VDC, 50 mA), selectable as Pulse output (external integration), flow rate high/low  alarm, count up/down, or alarm output

	Communication
	RS485 selectable (3-wire, Modbus transmission speed 19200 bps. max.)

	Electrical connection
	Cable PA5 Series VA connector (4 pins)

	Display
	7-segment, 5-digit display (instantaneous flow rate , cumulative flow, cost)

	Flow units
	Selectable: Nl/min, Nl, Nm3/h, Nm3 ,  Nm3/min, Nm3 , kg/h, kg

	Standards

	Ingress protection
	IP65. (Rating is based on JIS C 0920 and IEC529.)

	Standards compliance
	CE marked: EN61326-2-3: 2006

	Contact general: 
	Contact direct

	Azbil Europe NV
	Azbil Europe NV

	Bosdellestraat 120/2
	Martin Trojan

	B-1933 Zaventem / Belgium
	Tel: +49-(0)6202–574 198

	Tel: +32-(0)2-785 0710
	Fax: +49-(0)6202–574 199

	Fax:+32-(0)2-785 0711
	Mobil:+49-(0)151-1967 4551

	http://eu.azbil.com/
	m.trojan.nr@eu.azbil.com


Pressure loss (at gas pressure 100 – 700 kPa)

Selection guide:

	Model Number
	Code

	Basic
	Pipe size
	Material
	Pipe
	Gas
	Output
	Option
	Option
	Option
	Product
	Specification

	Model
	Range
	of body
	connect.
	type
	 
	 
	 
	 
	Version
	 

	MCF
	 
	 
	 
	 
	 
	 
	 
	 
	 
	Air/N2

	
	0080
	 
	 
	 
	 
	 
	 
	 
	 
	200 Nl/min (1/4")

	
	0150
	 
	 
	 
	 
	 
	 
	 
	 
	500 Nl/min (1/2")

	
	0151
	 
	 
	 
	 
	 
	 
	 
	 
	1.000 Nl/min (1/2" )

	
	0250
	 
	 
	 
	 
	 
	 
	 
	 
	3.000 Nl/min (1" )

	
	0400
	 
	 
	 
	 
	 
	 
	 
	 
	6.000 Nl/min ( 1 1/2")

	
	0500
	 
	 
	 
	 
	 
	 
	 
	 
	12.000 Nl/min (2")

	
	
	A
	 
	 
	 
	 
	 
	 
	 
	Alu-alloy NBR-seal

	
	
	F
	 
	 
	 
	 
	 
	 
	 
	Alu-alloy FKM-seal (oil inhibited)

	
	
	
	R
	 
	 
	 
	 
	 
	 
	Rc-Thread (female taper ISO 7-1)

	
	
	
	N
	 
	 
	 
	 
	 
	 
	NPT-Thread (female)

	
	
	
	G
	 
	 
	 
	 
	 
	 
	G-Thread (female cyl. ISO 228-1)

	
	
	
	
	N
	 
	 
	 
	 
	 
	Gas: Air / N2

	
	
	
	
	
	D01
	 
	 
	 
	 
	24VDC / 4-20 mA / Pulse

	
	
	
	
	
	D10
	 
	 
	 
	 
	24 VDC / RS 485 / no output

	
	
	
	
	
	
	0
	 
	 
	 
	None

	
	
	
	
	
	
	
	0
	 
	 
	None

	
	
	
	
	
	
	
	
	0
	 
	None

	
	
	
	
	
	
	
	
	D
	 
	Inspection Data

	
	
	
	
	
	
	
	
	Y 
	 
	Traceability Certificate

	
	
	
	
	
	
	
	
	
	0
	Style Code

	
	

	
	
	
	
	
	
	Cabel for MCF
	Connect-
	Cable Length

	
	
	
	
	
	
	Code
	 
	 
	ion
	[m]

	
	
	
	
	
	
	PA5-4ISX2MK-E
	M12
	2 m

	
	
	
	
	
	
	PA5-4ISX5MK-E
	M12
	5 m

	
	
	
	from 31.03.2011 please change code "M" into "S" while cable ordering (UL approved cable)

















Azbil Europe NV








AEU-MCF-01-01-2011        First Issue Jan. 2011

