1. Required part: 
81446803-002　Option board assembly unit for maintenance of　                                 



the P301/302 Honeywell version 81446806-001  (same as above)

2. Required work when replacing the part:


Please execute the general reset in the following steps:


1. 
Set the DCP301 to the READY AUTO mode.





Set the variable parameter LoC (key lock) and PrtC (program protect) to 0.


2.

If you press [FUNC] + [CLR] + [DISP] in the basic display state, the display 



changes to confirm execution of general reset, and “g.rES” is displayed on the upper display.


3.

If you press [ENT], the general reset is executed.


Operation starts from startup at power ON.


Note: 1.
Please refer to the page 8-15 of the DCP301 User’s Manual (No.EN11-6197) explaining 





the above general reset procedure.

2. The above work is not within the range of our assurance service, please tell the user so, 

and then execute the work. After the work, apply a label on the programmer to indicate that the above service was made.

