[image: image31.png]



[image: image1.jpg]i \\\\\\
\\ 11

\\\\\
\\\\\ Q, I
Water

\)

2007-337999/001 001 g "
Tohde B/BL DA
Fan TS

D: 1kgh

T:20°C

V: 1 mPas R

p: 1,013 bar





[image: image28.jpg]



Operating instructions
All rights reserved. It is prohibited to reproduce this documentation, or any part thereof, without the prior written authorisation of MECON Flow Control Systems GmbH.

Subject to change without notice.

Copyright 2011 by

MECON Flow Control Systems GmbH - Röntgenstraße 105 - 50169 Kerpen
Contents
1  Safety instructions
5

1.1
Intended use
5

1.2
Certifications
6

1.3
Safety instructions from the manufacturer
6

1.3.1
Disclaimer
6

1.3.2
Product liability and warranty
6

1.3.3
General information
7

1.4
Safety instructions for the operator
7
2  Device description
8

2.1
Scope of delivery
8

2.2
Device versions
8

2.2.1
Display unit made of aluminium
8

2.2.2
Display unit made of stainless steel
9

2.2.3
Heating sheath
9

2.2.4
Float damping
9

2.3
Nameplate
10

2.4
Description code
11

2.4.1
Individual part for versions CF-S and EF-H
11


2.4.2
Individual part for version FF-P
13


2.4.3
Common part for all versions
14

3  Installation
15

3.1
Notes on installation
15

3.2
Storage
15

3.3
Installation conditions
15

3.3.1
Tightening torques
17

3.3.2
Magnetic filters
17
4  Electrical connections
18

4.1
Safety instructions
18

4.2
Electrical connections
18

4.2.1
Limit switches
18

4.2.2
Current output (MEM)
19

4.2.3
Current output with digital outputs (MEM)
19

4.3
Protection category
21
5  Start-up
22

5.1
Standard device
22

5.2
Device with current output
22

5.3
Device with limit switches
23

6  Service
24

6.1
Maintenance
24

6.2
Replacing float damping
24

6.3
Replacing floats
25

6.4
Returning the device to the manufacturer
26

6.5
Disposal
26
7  Technical data
27

7.1
Operating principle
27

7.2
Classification
27


7.3
Technical data
28

7.4
Dimensions and weights
30
1  Safety instructions
1.1
Intended use

The series RE250 of flowmeters with a standard length of 250 mm (9.84 inch) and a completely metal design is suitable for measuring different liquids and gases in closed piping.
The robust design enables the operation in rough conditions also. Different types of flanges, liners and float materials satisfy the requirements of the pharmaceutical and chemical Indus​tries.

The devices are particularly suitable for the measurement of:

•
Water
•
Fluids

•
Corrosion protection agents

•
Lubricants

•
Saturated and superheated steam

•
Food and beverages

•
Industrial gases
	[image: image29.jpg]NG




 
	Warning!

Solely the operator of these measuring devices is responsible for suitability, intended use and corrosion resistance of the used mate​rials. It must be parti​cularly ensured that the materials selected for the wetted parts of the flow​meter are suitable for the used process media.

The manufacturer is not liable for any damage resulting from improper or unintended use of these devices.


No external loads may act upon the meter. The flowmeters are primarily designed for static applications.
	[image: image30.png]MECE®N

FLOW-CONTROL-SYSTEMS



 
	Caution!

Hot surfaces resulting from hot process media.
Danger of burns resulting from surface temperatures above 70 °C.

●
Take appropriate protective measures, for example contact protection.

●
The design of the contact protection must ensure here that the maximum permissible ambient temperature of the meter is not exceeded.
Caution!

For devices used in hazardous areas, additional safety notes apply; please refer to the Ex documentation!

	
	


The flowmeter may only be operated within the pressure and voltage limits specified on the name plate. 
Before replacing the flowmeters, check that the unit is free of hazardous media and pressures. 
1.2
Certifications
CE marking

[image: image2.jpg]



The manufacturer certifies for the device RE 250 the fulfilment of all statutory require​ments of the following EC directives by applying the CE marking:
•
Pressure equipment directive 97/23/EC 

•
Low voltage directive 2006/95/EC
 *


•
EMC-directive 89/336/EEC
•
NAMUR recommendation NE21 *
•
ATEX directive 94/9/EC **
(*
Devices with electrical installations)       (**
Devices for use in hazardous areas)
1.3
Safety instructions from the manufacturer
1.3.1
Disclaimer
The manufacturer will not be liable for any damage using its product, including, but not limited to direct, indirect, incidental, punitive and consequential damages.

Any product purchased from the manufacturer is warranted in accordance with the relevant product documentation and our Terms and Conditions of Sale.

The manufacturer reserves the right to revise the content of its documents, including this disclaimer, without prior notification, and will not be liable in any way for possible consequences of such changes.
1.3.2
Product liability and warranty

Mecon GmbH can assume no guarantee for repair work carried out by the custo​mer without prior notification and consultation. In case of complaint, the rejected parts must be returned to us, if no other arrangement has been made.
1.3.3
General information
This manual is intended for correct installation as well as operation and maintenance of the devices. Read the instructions carefully before installing the device and put it into operation.
Specially designed or customised models and specialised applications are not included in this manual. 
1.4
Safety instructions for the operator
	 
	Warning!

Hot surfaces resulting from hot process media.

Danger of burns resulting from surface temperatures above 70 °C.

●
Take appropriate protective measures, for example contact protection.

●
The design of the contact protection must ensure here that the maximum permissible ambient temperature of the meter is not exceeded.
Caution!

For devices used in hazardous areas, additional safety notes apply; please refer to the Ex documentation!

	


	 
	


2  Device description
2.1
Scope of delivery
[image: image3.jpg]



Fig 2.1 
Scope of delivery
	(
	Information!

Please check the delivery for completeness using the packing list. 


2.2
Device versions
2.2.1
Display unit made of aluminium
[image: image4.jpg]D: kol
T 20°C
Vi 1mPas
pe: 0 bar





Fig. 2.2
Standard device with display unit made of aluminium

The measured value is indicated directly on the scale. The equipment can be supplied with accessory electrical components and touch-sensitive switches for process monitoring and control.
2.2.2
Display unit made of stainless steel

[image: image5.jpg]



Fig. 2.3
Standard device with display unit made of stainless steel

For applications with the requirements of higher protection category or corrosion resistance the devices are available with a display unit made of stainless steel.
2.2.3
Heating sheath
[image: image6.jpg]90 100
70 80

[

D: 1kgl

T 20°C

V. 1mPas

pe: 0 bar
]
SR





Fig. 2.4
Device with heating sheath

For measuring points where a temperature drop is unacceptable the devices are available with an external heating sheath. 
2.2.4
Float damping
A float damping is recommended

●
Generally for measuring gases
●
Vibrations for the piping cannot be avoided 

It is also strongly recommended in the case of 
●
applications where air bubbles in the medium cannot be avoided

●
predominating shock pressure in the piping, e.g. due to rapid throttling or shut-off

●
turbulences, pulsations, etc. which could lead to vibrations to the flowmeter
●
rapid pressure build-up in the piping
2.3
Nameplate
	 
	Important!

Please refer to the device nameplate to ensure that the device is built according to your order.
Check particularly for the correct supply voltage.

	


[image: image7.jpg]OIOICIOICICIOIOLC)

LI

D-50169
Kerpen

N

MEC® N

FLOW-CONTROL-SYSTEMS

RE 250

— RE250x-XxxxX-XXX-XXX-XXxxX PED xxx/G1/L4+—
~ XXXX-XXXXXX/XXX XXX 97/23/EG

c E 0045

~~ Connection:
— Material
—PS

— TS Medium :

XXXXXXXXXXXXXXXXXXXX
XXXXXXXXXX

xx bar / xxx psi

xxx °C / xxx °F

T max =xx °C

— Protection EN 60529: IP65
XXX XXXXXX XXX XXX XXX X
—{ XXXXXXXXXXXXXXXXXXXXXX

Code number

Made in Germany

Device specific code number

Year / Serial number Device specific serial number and the year it was built
Connection Connection type of the device

Material Material of the wetted parts

PS Maximum pressure of the medium

TS Medium Maximum temperature of the medium

Protection Protection class for the housing of display

MEM specification
Category

Electrical specifications of the output / transducer (MEM)

Category acc. to Pressure Equipment directive (PED)




Fig. 2.5
Nameplate of the RE250
2.4
Description code
2.4.1
Individual part for versions CF-S (stainless  steel) and EF-H (Hastelloy®)
The description code consists of the following elements:
[image: image8.jpg]



	1
Flow tube

	A
	Nominal size flow tube DN 15

	B
	Nominal size flow tube DN 25

	C
	Nominal size flow tube DN 40

	D
	Nominal size flow tube DN 50

	E
	Nominal size flow tube DN 80

	F
	Nominal size flow tube DN 100

	2
Version

	1
	CF-S
wetted parts: stainless steel

	2
	EF-H
wetted parts: Hastelloy®

	3
Process connections

	
	EN1092-1
	ANSI B16.5
	
	Flow tube EN
	Flow tube ANSI

	
	
	
	
	A
	B
	C
	D
	E
	F
	A
	B
	C
	D
	E
	F

	          Nominal size
	Axx
	DN 15
	½ ”
	
	(
	(
	
	
	
	
	(
	(
	
	
	
	

	
	Bxx
	DN 20
	¾ ”
	
	(
	(
	(
	
	
	
	(
	(
	
	
	
	

	
	Cxx
	DN 25
	1 ”
	
	(
	(
	(
	
	
	
	(
	(
	(
	
	
	

	
	Dxx
	DN 32
	1 ¼ ”
	
	(
	(
	(
	(
	
	
	(
	(
	(
	
	
	

	
	Exx
	DN 40
	1 ½ ”
	
	(
	(
	(
	(
	
	
	(
	(
	(
	(
	
	

	
	Fxx
	DN 50
	2 ”
	
	(
	(
	(
	(
	
	
	(
	(
	(
	(
	
	

	
	Gxx
	DN 65
	2 ½ ”
	
	
	(
	(
	(
	(
	
	
	(
	(
	(
	(
	

	
	Hxx
	DN 80
	3”
	
	
	
	(
	(
	(
	(
	
	
	(
	(
	(
	

	
	Jxx
	DN 100
	4”
	
	
	
	
	(
	(
	(
	
	
	
	(
	(
	(

	
	Kxx
	DN 125
	5”
	
	
	
	
	
	(
	(
	
	
	
	
	(
	(

	
	Lxx
	DN 150
	6”
	
	
	
	
	
	(
	(
	
	
	
	
	(
	(

	
	
	
	
	( = available      ( = reduced scale raised face

	

	Pressure rating
	xBx
	PN 16
	(EN 1092-1)
	
	DN 65 - DN 150

	
	xDx
	PN 40
	(EN 1092-1)
	
	DN 65 - DN 150

	
	xEx
	PN 63
	(EN 1092-1)
	
	DN 65 - DN 150

	
	xFx
	PN 100
	(EN 1092-1)
	
	DN 65 - DN 150

	
	xHx
	150 lbs
	(ASME B16.5)
	
	½ ” – 6 ”

	
	xJx
	300 lbs
	(ASME B16.5)
	
	½ ” – 6 ”

	
	xKx
	600 lbs
	(ASME B16.5)
	
	½ ” – 6 ”

	

	Flange form
	xxA
	B1
	(EN 1092-1)
	
	PN 16 / PN 40

	
	xxB
	B2
	(EN 1092-1)
	
	PN 63 / DN 100

	
	xxC
	Form D
	(EN 1092-1)
	
	DN 15 - DN 150

	
	xxD
	Form C
	(EN 1092-1)
	
	DN 15 - DN 150

	
	xxG
	Form RF
	(ASME B16.5)
	
	½ ” – 6 ”

	
	xxH
	Form FF
	(ASME B16.5)
	
	½ ” – 6 ”

	
	xxJ
	Form RTJ
	(ASME B16.5)
	
	½ ” – ¾”
150 lbs not available





	4
Heating sheath

	0
	Without

	1
	With flange connection DN 15 DIN 2501 PN 40 in stainless steel

	2
	With flange connection DN 25 DIN 2501 PN 40 in stainless steel

	3
	With flange connection ½ “ ANSI B16.5 150 RF in stainless steel

	4
	With flange connection 1 “  ANSI B16.5 150 RF in stainless steel




	5
Maximum range values / Measuring ranges

	
	Fluids 
	Gases 
	Ratio
	Viscosity
limits*
	Pressure drop [mbar] 

	
	[l/h]
	[USgpm]
	[m³/h]
	[scfm]
	
	[mPa(s]
	A
	B
	C
	D
	E
	F

	1
	5
	0,022
	0,15
	0,088
	1:10
	≤ 1,0
	40
	(
	(
	(
	(
	(


	2
	10
	0,044
	0,30
	0,177
	1:10
	≤ 1,0
	44
	(
	(
	(
	(
	(

	3
	16
	0,07
	0,48
	0,283
	1:10
	≤ 1,0
	40
	(
	(
	(
	(
	(

	4
	25
	0,11
	0,75
	0,441
	1:10
	≤ 1,0
	40
	(
	(
	(
	(
	(

	5
	40
	0,18
	1,3
	0,765
	1:10
	≤ 1,0
	40
	(
	(
	(
	(
	(

	A
	50
	0,22
	1,5
	0,883
	1:10
	≤ 1,0
	40
	(
	(
	(
	(
	(

	B
	70
	0,31
	2,1
	1,24
	1:10
	≤ 1,0
	40
	(
	(
	(
	(
	(

	C
	100
	0,44
	3,0
	1,77
	1:10
	≤ 1,0
	60
	(
	(
	(
	(
	(

	D
	160
	0,70
	4,6
	2,71
	1:10
	1 … 3
	60
	(
	(
	(
	(
	(

	E
	250
	1,10
	7,0
	4,12
	1:10
	1 … 3
	60
	(
	(
	(
	(
	(

	F
	400
	1,76
	11
	6,47
	1:10
	1 … 3
	70
	(
	(
	(
	(
	(

	G
	600
	2,64
	17
	10,00
	1:10
	1 … 5
	80
	(
	(
	(
	(
	(

	H
	1000
	4,40
	30
	17,66
	1:10
	1 … 5
	(
	60
	(
	(
	(
	(

	J
	1600
	7,0
	46
	27,07
	1:10
	1 … 5
	(
	70
	(
	(
	(
	(

	K
	2500
	11,0
	70
	41,20
	1:10
	1 … 5
	(
	100
	50
	(
	(
	(

	L
	4000
	17,6
	110
	64,74
	1:10
	1 … 8
	(
	240
	120
	80
	(
	(

	M
	6000
	26,4
	170
	100,0
	1:10
	1 … 8
	(
	(
	180
	90
	(
	(

	N
	10.000
	44,0
	290
	170,7
	1:10
	1 … 8
	(
	(
	(
	110
	(
	(

	P
	16.000
	70,0
	460
	270,7
	1:10
	1 … 10
	(
	(
	(
	230
	70
	(

	Q
	20.000
	88,0
	550
	323,7
	1:10
	1 … 10
	(
	(
	(
	230
	70
	(

	R
	25.000
	110,0
	700
	412,0
	1:10
	1 … 10
	(
	(
	(
	500
	100
	(

	S
	40.000
	176,0
	1.100
	647,4
	1:10
	1 … 15
	(
	(
	(
	(
	350
	120

	T
	50.000
	220,0
	1.350
	794,6
	1:10
	1 … 15
	(
	(
	(
	(
	350
	120

	U
	60.000
	264,0
	1.700
	1.000
	1:10
	1 … 25
	(
	(
	(
	(
	(
	360

	V
	80.000
	352,0
	2.400
	1.413
	1:10
	1 … 25
	(
	(
	(
	(
	(
	600

	W
	100.000
	440,0
	3.000
	1.766
	1:10
	1 … 25
	(
	(
	(
	(
	(
	600

	* devices for media with higher viscosity on request
( = not available 




	6
Measured medium

	1
	Water ((= 1 mPa(s, ( = 1 kg/l)

	2
	Air (T = 20 °C, pe = 0 bar, (= 0.0181 mPa(s, ( = 1,293 kg/m³)

	3
	Specify in plain text




	7
Float damping

	0
	Without float damping

	1
	With float damping


2.4.2
Individual part for version FF-P (PTFE liner)

The description code consists of the following elements:

[image: image9.jpg].
.

.

9





	1
Flow tube

	A
	Nominal size flow tube DN 15

	B
	Nominal size flow tube DN 25

	C
	Nominal size flow tube DN 40

	D
	Nominal size flow tube DN 50

	E
	Nominal size flow tube DN 80

	F
	Nominal size flow tube DN 100

	3
Process connections
 

	
	
	EN1092-1

	ANSI B16.5

	Flow tube EN
	Flow tube ANSI

	Nominal Size
	
	
	
	A
	B
	C
	D
	E
	F
	A
	B
	C
	D
	E
	F

	
	Axx
	DN 15
	½ ”
	(
	
	
	
	
	
	(
	
	
	
	
	

	
	Cxx
	DN 25
	1 ”
	
	(
	
	
	
	
	
	(
	
	
	
	

	
	Exx
	DN 40
	1 ½ ”
	
	
	(
	
	
	
	
	
	(
	
	
	

	
	Fxx
	DN 50
	2 ”
	
	
	
	(
	
	
	
	
	
	(
	
	

	
	Hxx
	DN 80
	3”
	
	
	
	
	(
	
	
	
	
	
	(
	

	
	Jxx
	DN 100
	4”
	
	
	
	
	
	(
	
	
	
	
	
	(

	
	

	Pressure

rating
	xBx
	PN 16 B1
	(EN 1092-1)
	
	DN 100

	
	xDx
	PN 40 B1
	(EN 1092-1)
	
	DN 15 - DN 100

	
	xHx
	150 lbs
	(ASME B16.5)
	
	½ ” – 4 ”

	
	xJx
	300 lbs
	(ASME B16.5)
	
	½ ” – 4 ”

	
	
	
	
	
	

	Flange  
form 
	

	
	xxA
	B1
	(EN 1092-1)
	
	PN 16 / PN 40

	
	xxG
	Form RF
	(ASME B16.5)
	
	½ ” – 4 ”

	
	




	5
Maximum range values / Measuring ranges

	
	Fluids 
	Gases
	Ratio
	Viscosity
limits*
	Pressure drop [mbar]

	
	[l/h]
	[USgpm]
	[m³/h]
	[mPa(s]
	
	[mPa(s]
	A
	B
	C
	D
	E
	F

	C
	100
	0,44
	3,0
	1,77
	1:10
	≤ 1,0
	60
	60
	(
	(
	(
	(

	D
	160
	0,70
	4,6
	2,71
	1:10
	1 … 3
	60
	60
	(
	(
	(
	(

	E
	250
	1,10
	7,0
	4,12
	1:10
	1 … 3
	60
	60
	(
	(
	(
	(

	F
	400
	1,76
	11
	6,47
	1:10
	1 … 3
	70
	70
	(
	(
	(
	(

	G
	600
	2,64
	17
	10,00
	1:10
	1 … 5
	80
	80
	(
	(
	(
	(

	H
	1000
	4,40
	30
	17,66
	1:10
	1 … 5
	(
	60
	(
	(
	(
	(

	J
	1600
	7,0
	46
	27,07
	1:10
	1 … 5
	(
	70
	(
	(
	(
	(

	K
	2500
	11,0
	70
	41,20
	1:10
	1 … 5
	(
	100
	50
	(
	(
	(

	L
	4000
	17,6
	110
	64,74
	1:10
	1 … 8
	(
	(
	120
	80
	(
	(

	M
	6000
	26,4
	170
	100,0
	1:10
	1 … 8
	(
	(
	(
	90
	(
	(

	N
	10.000
	44,0
	290
	170,7
	1:10
	1 … 8
	(
	(
	(
	110
	(
	(


	P
	16.000
	70,0
	460
	270,7
	1:10
	1 … 10
	(
	(
	(
	230
	70
	(

	Q
	20.000
	88,0
	550
	323,7
	1:10
	1 … 10
	(
	(
	(
	230
	(
	(

	R
	25.000
	110,0
	700
	412,0
	1:10
	1 … 10
	(
	(
	(
	(
	100
	(

	S
	40.000
	176,0
	1.100
	647,4
	1:10
	1 … 15
	(
	(
	(
	(
	(
	120

	* devices for media with higher viscosity on request 
( = not available




	6
Measured medium

	1
	Water ((= 1 mPa(s, ( = 1 kg/l)

	2
	Air (T = 20 °C, pe = 0 bar, (= 0.0181 mPa(s, ( = 1,293 kg/m³)

	3
	Specify in plain text


2.4.3
Description code – common part for all versions

The description code consists of the following elements:

[image: image10.jpg]Ty 5 @ A AT @ 1) @ 13 @9 1>






	8
Display unit / Process temperature

	0
	Standard (aluminium)
– up to 200 °C for local display / 150 °C for electric output)

	1
	Standard (aluminium)
– with displaced display (extension made of stainless steel) 

	2
	Stainless steel IP66
– up to 150 °C

	3
	Stainless steel IP66
– with displaced display




	9
Outputs

	A A
	With local display

	C J
	With local display, 1 inductive contact SJ 3,5N

	C L
	With local display, 2 inductive contacts SJ 3,5N

	E A
	With local display, electric remote sensor 4 - 20 mA

	E L
	With local display, electric remote sensor 4 - 20 mA, 2 inductive contacts SJ 3,5N

	E J
	With local display, electric remote sensor 4 - 20 mA, 1 inductive contact, 1 pulse output

	F A
	With HART protocol, 4 - 20mA

	F L
	With HART protocol, 4 - 20mA, 2 inductive contacts SJ 3,5N

	F J
	With HART protocol, 1 inductive contact, 1 pulse output

	P A
	With PROFIBUS PA interface 




	 10
Certification of accuracy

	0
	Without calibration certificate

	1
	Certification of accuracy class (4.2.1)

	2
	With calibration report (5 calibration points)

	3
	With calibration report (10 calibration points)




	 11
Leak / pressure test

	0
	Without leak/pressure test

	1
	Pressure test acc. to EN 10204 with inspection certificate 3.1

	2
	Leak test acc. to EN 10204 with inspection certificate 3.1

	3
	Pressure test + leak test (acc. to EN 10204 with inspection certificates 3.1) 




	 12
Material certificates

	A
	Without certificate

	B
	Certificate of Compliance with the Order 2.1 according to DIN EN 10 204

	C
	Inspection certificate 3.1 with material analysis (DIN EN 10204:2004) for wetted parts




	 13
Cleaning to factory standard

	A
	Without cleaning

	B
	Cleaning class VA – with marking: free from oil and grease

	C
	Cleaning class VA – with marking: free from oil, grease and silicone 




	 14
Approvals

	0
	Without

	1
	Explosion protection – mechanical approval ATEX xxxx

	2
	Explosion protection – mechanical and electrical (MEM/MEM-PPA) approval ATEX xxxx




	 15
Marking

	0
	Without marking

	1
	Cardboard plate with a cable tie

	2
	Stainless steel plate (dimensions 40 x 20mm)

	3
	Cardboard plate with cable tie + stainless steel plate (dimensions 40 x 20 mm)


3  Installation

3.1
Notes on installation
	(
	Information!

All instruments are carefully checked for functional capability before distribution. On receipt of the device please carry out a visual inspec​tion of the outer packing for damage or improper handling.
Please contact the carrier and your responsible sales field service if you should disco​ver any defects. In such cases a description of the defect, the type and the serial number of the device is needed.

	(
	Information!

Unpack the equipment with care to prevent damage.

	(
	Information!

All instruments are carefully checked for order conformity.

Please check the delivery for completeness using the packing list. Please examine the flowmeter nameplate to verify that the device was built according to your order. Particularly check devices with electrical components for the correct supply voltage.


3.2
Storage
●
Store the device in a dry and dust-free place.

●
Keep away from direct sun and heat.

●
Avoid external load to the device.

●
The storage temperature range for standard devices with electrical components is about -40 … +70 °C / -40 … +158 °F. 

3.3
Installation conditions
Below the essential points concerning installation are described and have to be observed:

●
Remove the transport securing device from the fitting.
●
Verify prior to installation that the float slides smoothly in the fitting without canting or deadlocking. The pointer must smoothly follow the float movement. 
●
Verify that accessories such as spring stop, gas/fluid damping are still correctly fixed in the fitting.

●
In the zero position (no flow) the pointer must be at the marked reference point (first line on the scale). When moving the float manually to the end position, the pointer must be above the final value of the scale.

●
The flowmeter must be installed vertically – flow direction from bot​tom to top. For installation recommendations refer to guideline VDI/VDE 3513 Part 3.

●
The installation in the piping must be tension-free – therefore the piping must be positioned parallel and aligned to each other. 
●
Avoid a corrosive atmosphere –provide a ventilation where necessary.

●
Ensure a sufficient distance of at least 200 mm to magnet-influencing parts like e.g. solenoid valves and ferromagnetic components e.g. steel brackets.
●
Observe a lateral distance of at least 300 mm between two next to one another mounted devices. The distance can be reduced by mounting the devices staggered by the length of one device. In case of doubt the influence can be tested by mo​ving the instrument up and down ca. 200 mm at a selected distance and check whether the position of the pointer in the display changes.
●
Specify the installation zone regarding a reliable reading of the displayed values and adequate space for servicing.
●
An inlet run upstream and an outlet run downstream the device is not necessary in the case of linear media flow profile. In the case of highly asymmetric flow profiles, however, additional measures (e.g. inlet tracks, flow rectifiers) with a length of at least 250 mm could be appropriate to ensure the measuring accuracy.
●
Avoid the installation of unilaterally constricting fittings upstream of the device.
●
Ensure that the piping has been mounted securely to avoid vibration or oscillation of the devices.
●
The nominal width of the flowmeter and the connected piping must be identically.
●
Use connectors suitable for the particular device version (dimension, pressure stage).
●
Ensure that the clearance between the flanges of the piping corresponds to the device dimension additionally two gaskets.

●
Before connecting the device, blow or flush out the pipes leding to the device.

●
The surface roughness of the flange sealing areas must be appropriate for the used gaskets. 

●
The used gaskets and bolts of the prescribed dimensions must be appropriate for the operating pressure, the temperature and the media.

●
Do not use carbon steel mounting brackets for the device!
Additionally for devices with PTFE liner:

●
Use gaskets which are conform to the inner and outer dimensions with the raised face of the flowmeter.
 ●
Tighten the screws crosswise to ensure the tightness of the process connections. For the tightening torques please refer to chapter “3.3.1 Tightening torques”.
●
If the instrument is absolutely calibrated for a pressure exceeding 1.013 bar the valve is usually installed at the rear of the flowmeter, at 1.013 bar absolute (free emanation) in front of the instrument.
Particularities for measuring gas flow:

●
Valves have to be installed downstream of the device if pabs >1.013 bar and upstream of the device if pabs =1.013 bar (free outflow) usually.
●
Install a throttle just downstream of the device to prevent compression oscillation during measurement.
●
Ensure by means of design features that the operating pressure for the flowmeter corresponds to the reference pressure of the calibration to avoid erroneous measurements.
3.3.1
Tightening torques
The flange bolts for devices with PTFE liner may be tightened with the following torques (acc. guideline VDI/VDE 3513):
	Process connection
	max. torque

	EN1092-1
	ANSI B16.5
	Nm
	ft(lbf

	15
	½”
	14
	10

	25
	1”
	14
	10

	40
	1 ½”
	25
	18

	50
	2”
	25
	18

	80
	3”
	35
	25

	100
	4”
	42
	30


Tab 3.1 
Tightening torques for devices with PTFE liner
3.3.2
Magnetic filters
To prevent a malfunction of the flowmeter caused by a medium which contains ferromagnetic substances such as weld beads a magnetic filter should be mounted in flow direction upstream of the measuring instrument.

This kind of filter is also recommended if such particles cannot be avoided in standard operation.
4  Electrical connections
4.1
Safety instructions
	 
	Warning!

All work on the electrical connections may only be carried out by a specialist. Ensure that the power is disconnected. 

Observe all occupational safety regulations unconditionally. It is essential to regard the voltage data on the nameplate.


4.2
Electrical connections
The display lid can be removed by loosen the four mounting screws at the front. In​sert the connection cable through the cable gland at the baseplate. The RE250 is equipped with screw terminals. 
4.2.1
Limit switches
[image: image11.jpg]



[image: image12.jpg]



Fig 4.1
Terminals (one limit switch)
Fig 4.2
Terminals (two limit switches)
[image: image13.jpg]Hazardous area

Inductive contact
SJ3,5-N

Safe area

Isolation amplifier

I O

o Lo

Max. limit value
#

Contact according to
EN 60947-5-6
(NAMUR)

N

4& Auxiliary power supply





Fig 4.3
Connection diagram for RE250 with one limit switch

[image: image14.jpg]Hazardous area

Inductive contact

Safe area

Contacts according to
EN 60947-5-6
(NAMUR)

[
[
[
[
SJ3,5-N : Isolation amplifier
+ A1 | +
| > | #
[
O Ll | - *
O i
[
[
+] ~3 | +
| = : )
O | Lot ! , / #
[ ;
[
[
!

Min. limit value

Max. limit value

4 Auxiliary power supply





Fig 4.4
Connection diagram for RE250 with two limit switches
4.2.2
Current output (MEM)

[image: image15.jpg]Nicht belegt
no connect

current loop
i = 150 mA
i = 1W





[image: image16.jpg]



Fig 4.5
Terminals (current output)
Fig 4.6
Terminals (with add. digital outputs)

[image: image17.jpg]Angular sensor

Hazardous area

|
|
|
|
type MEM :
1 | =
Ao+ |
4-20 mA |
5 | _
E 1O [
|
|
Supply current circuit | Auxiliary power supply
Li = 240pH Ui = 30V '
Ci=16nF li = 150 mA |
Ta = 70°C Pi = 1000 mW |
EEx ia IIC T6 :
|

Safe area

Transmitter power supply

BVS 07 ATEX E 033

E

/

E

Output 4 -20 mA

Ra




Fig 4.7
Connection diagram for transducer MEM with current output

4.2.3
Current output with digital outputs (MEM)

[image: image18.jpg]Hazardous area

Supply current circuit

Safe area

BVS 07 ATEXE 033

|
|
|
Li = 240pH Ui = 30V :
Ci = 16nF  li = 150 mA Transmitter power supply
Ta = 70°C  Pi = 1000 mwW |
EEx ia IIC T6 | + E
Angular sensor BVS 07 ATEXE 033 |
type MEM : E 4 -20 mA
f ol + _01 : = /
4-20mA | i
o2 |
| Auxiliary power supply
3 |
MAX :4 [
# 1O ! Isolation amplifier
5 | N
# ——
MIN _06 | ] \ MAX limit value
# O | # bbb
| o
Contacts according to : | #
EN 60947-5-6 ~ EinamiouipuG | |8 2 MIN limit value
(NAMUR) Li = 4pH U = 30V )
Ci = 16nF  li = 20mA |
Ta = 70°C Pi = 100mw |
EEx ia IIC T6 | Auxiliary power supply
|
|




Fig 4.8
Connection diagram for transducer MEM with 2 limit switches
[image: image19.jpg]Hazardous area

Supply current circuit

Safe area

Transmitter power supply

E

\

i

4-20 mA

4 Auxiliary power supply

Isolation amplifier

=

BVS 07 ATEX E 033

AN

I
I
I
Li = 240uH Ui = 30V '
Ci = 16nF li = 150 mA |
Ta = 70°C  Pi = 1000mw |
EExia llC T6 | +
Angular sensor BVS 07 ATEX E 033 |
type MEM |
I
ﬁ o+ _01 | -
I
4-20 mA |
2
E [© :
3 I
TULL —O I
# _04 |
5 | -
MIN —O I
# o8 ! :
| %
Contacts according to : [
Binary outputs )
E’\(IN6A?I\9/I?J7I§)S_6 Li = 4pH Ui = 30V |
Ci = 16nF i = 20mA |
Ta = 70°C Pi = 100mw |
EExia llC T6 :
|

#

#/

Pulse output

MIN/MAX limit value

4 Auxiliary power supply





Fig 4.9
Connection diagram for transducer MEM with limit switch and pulse output
4.3
Protection class
The realised protection class of the display unit made of aluminium is class IP65. The version made of stainless steel will meet all requirements of protection class IP66.
	 
	Caution!

After installation and any maintenance work on the device, the operator has to check and ensure the specified protection class again.

	

	
	Therefore pay regard to the following issues:

●
Mounting screws of the display unit must be tightened.

●
All gaskets (display unit and cable glands) have to be undamaged. Broken gaskets have to be replaced.
●
The electrical cable glands must be free of any damage and tightened. Broken cable glands have to be replaced.

●
Install the cables with a loop in front of the cable glands so that moisture does not get inside the display unit (refer to Fig. 4.5).

[image: image20.jpg]





Fig 4.10
Installing the cables in front of the cable glands (loop)
5  Start-up

5.1
Standard device
When starting up the device, the following points must be observed:
●
Ensure that the actual operation conditions (pressure, temperature) do not exceed the limits which are given on the nameplate of the device
●
Avoid float impacts!

Therefore it is recommended to start up with a closed shut-off valve and open it slowly. Particularly the use of solenoid valves is not recommended.
●
When measuring liquids, the pipes must be vent slowly to prevent shock pressure due to gas bubbles.
●
When measuring gases, the pressure must be increased slowly in order to prevent high shock pressure.
●
During the start-up of new systems, residual materials are conveyed in the medi​um and could adhere to the float. In this case we recommend cleaning the instru​ment after a relatively short period of operation.
●
When operating the flowmeter at low flowrates, the device has to start-up with a high flowrate to allow the float to level out. This will ensure measurements within the specified accuracy class.
5.2
Device with current output (MEM)
The magneto-electrical measuring transducer (MEM) is completely factory-set when it is delivered to the customer.

After applying the supply voltage to the device, initially the current output will be about 3.5 mA to 4 mA for a few seconds. After that a current corresponding to the pointer deflection will flow.
	(
	Important!

Due to the influence of the float magnet, the MEM transmitter will only output the correct current if the pointer position is caused by the float. Turning the pointer manually will cause incorrect values, but it’s suitable for testing the unit.


5.3
Device with limit switches

The limit switches can be set over the entire measuring range by varying the position the limit pointers.
	(
	Important!

Unless otherwise desired by the customer, the factory set value for the switching point is for version with one limit switch about 40% of URV and for devices with two limit switches about 20% / 80% of URV.


To set the limit switches at the desired position the following step have to be observed:

●
Unloosen the two little fixing screws 2 before moving the pointer 1. 
●
Move the pointer to the desired position.

●
Tighten the screws to fix the pointer.
[image: image21.jpg]



Fig 5.1
Adjustment of the switching point (limit switch)

	(
	Important!

The applied limit switches SJ 3,5 N are normally closed contacts accor​ding to NAMUR recommendation NE21. The desired switching function of the limit switch has to be realized by the relay contact of the exter​nal isolation amplifier (changeover contact).


6  Service

6.1
Maintenance
The devices were built within the scope of low maintenance but periodically the flow​meters should be inspected for signs of corrosion, mechanical wear as well as da​mage to the fitting and the display unit.
We advice to carry out inspections at least once a year.

For a detailed inspection and cleaning the device must be removed from the piping.

	 
	Caution!

Appro​priate safety precautions have to be taken when removing the device. Always use new gaskets when reinstalling the device in the piping. 




6.2
Replacing float damping
Devices with measuring ring

For devices with standard measuring ranges starting from 5-50 l/h (gases: 0.15 – 1.5 m³/h) the float damping can be replaced by the customer:
●
Remove the device from the piping.
●
Fix the device, ensuring that the fitting will not be damaged.

●
The damping cylinder (  is fixed by re​taining clamps (. Bend up these two clamps carefully using a suitable tool.
●
Move the damping cylinder a little bit to the bottom end of the fitting, make a quarter turn and take the cylinder out of the fitting.
●
Insert the new damping cylinder into the fitting from the top, slide it over the damping part of the float and arrange it into the retaining clamps.

●
Fix the cylinder by bending the retaining clamps together.

●
Fit the device back into the piping.

6.3
Replacing floats
Devices with measuring ring

For devices with standard measuring ranges starting from 5-50 l/h (gases: 0.15 – 1.5 m³/h) the replacement of the float can be provided by the customer:
●
Remove the device from the piping.
●
Fix the device ideally in a horizontal position, ensuring that the fitting will not be damaged.

●
Prevent the float ( from torsion by fixing the upper guide bracket ( using a suitable tool. 
●
Remove the self-locking ( nut which fix the lower guide bracket ( and take the guide bracket out of the fitting. 
●
Take the float out of the measuring unit upwards.
●
Insert the new float into the fitting from the top. While doing so put the bottom end of the float through the measuring ring carefully. 

●
Slip the lower guide bracket through the tread at the bottom end of the float and fix it with the self-locking nut.

●
Fit the device back into the piping.
	 
	Important! 

Avoid damaging both float and measuring ring.



	
	Important! 

After the replacement of the float a recalibration of the flowmeter is highly recommended, otherwise the measurement accuracy can’t be ensured.


Devices with cone 
●
Replacing floats for devices with cone (standard measuring ranges up to 5-50 l/h (gases: 0.15 – 1.5 m³/h) cannot be provided by the customer. For this purpose the device has to be returned to the manufacturer. For details please refer to chapter “6.4 Returning the device to the manufacturer”.
6.4
Returning the device to the manufacturer
This device has been carefully manufactured and tested. Should you nevertheless need to return a device to MECON GmbH please observe the following points:
	 
	Caution!

According to the actual waste disposal directives, the owner/customer is responsible for the waste management of hazardous and toxic waste.
For reasons of environmental protection and safeguarding the health and safety of our personnel all devices sent to MECON GmbH to be repaired must be free of toxic and hazardous substances. This also applies to cavities of the devices. If necessary the customer is kindly requested to neutralize or rinse the devices before returning to MECON.
The customer has to confirm this by filling in an appropriate form which is available for download on the MECON website: 

www.mecon.de/en/declaration/contamination.pdf



	 
	Caution!

In the case of returning devices, despite these requirements, which contain hazardous and toxic substances, Mecon GmbH is entitled to dispose these substances at the cost of the customer without any further inquiries.




6.5
Disposal
	 
	Caution!

Disposal of the devices has to be carried out in accordance with relevant legislation in your country.




7  Technical data

7.1
Operating principle
Like other devices of this series the variable area flowmeter RE250 operates on the principle of flotation:
The measuring unit consists of a metal tube with a measuring ring in which a float can move up and down. The media is flowing upwards through the tube and raises the conical float. Here the annular gap enlarges until the equilibrium between the buoyancy force FA, the drag force FS and the weight of the float FG has been reached. The adjusted height of the float is directly proportional to the flowrate. The movement of the float is transmitted via a magnet to a subsequent magnet in the display unit outside the measuring pipe.
[image: image22.jpg]SN NN N N N N N N N N N N N N N
\

= | o]
\

\
NN N N N N N N N N N N N N N N N Y N N N N N N N N N N

NN N N N N N N N N N N N N N N N NN

C N
yJ

BN N N N N N N N





Fig. 7.1
Operating principle of the RE250

7.2
Classification

Classification in accordance with the Pressure Equipment Directive (PED) 97/23/EC:
	Process connection
	Admissible media
	Category

	EN1092-1
	ANSI B16.5
	
	

	DN 15
	½ ”
	Gases and fluids of fluid group 1
	Art. 3.3

	DN 20
	¾ ”
	Gases and fluids of fluid group 1
	Art. 3.3

	DN 25
	1 ”
	Gases and fluids of fluid group 1
	Art. 3.3

	DN 32
	1 ¼ ”
	Gases and fluids of fluid group 1
	III

	DN 40
	1 ½ ”
	Gases and fluids of fluid group 1
	III


	DN 50
	2 ”
	Gases and fluids of fluid group 1
	III

	DN 65
	2 ½ ”
	Gases and fluids of fluid group 1
	III

	DN 80
	3”
	Gases and fluids of fluid group 1
	III

	DN 100
	4”
	Gases and fluids of fluid group 1
	III

	DN 125
	5”
	Gases and fluids of fluid group 1
	III

	DN 150
	6”
	Gases and fluids of fluid group 1
	III


Tab 7.1 
Classification in accordance with PED 97/23/EC 
7.3
Technical data
General data
	Range of application
	Flow measurement of liquids and gases

	Measuring principle
	Flotation / Float measuring

	Orientation
	Vertical – flow direction from bottom to top


Measuring accuracy*
	Directive
	VDI / VDE 3513, sheet 2 (qG = 50%)

	Liquids
	G 1.6 (add. 0,2 %** of URV for MEM / MEM-PPA)

	Gases
	G 2.0 (add. 0,2 %** of URV for MEM / MEM-PPA)

	Reproducibility
	0,5 % of URV (add. 0,1 % of URV for MEM / MEM-PPA)


*   A variation of the operating temperature to the considered temperature for the calibration process, will lead to a corresponding inherent error
** For ambient temperatures < -20 °C the measuring error will increase
Materials

	
	Type CF-S
	Type EF-H
	Type FF-P

	Wetted parts
	Stainless steel
	Hastelloy®
	PTFE

	Flange
	<= DN 25 (1”)
	Stainless steel
	Hastelloy®
	Stainless steel

	
	> DN 25 (1”)
	
	Hastelloy® stainless
	

	Fitting
<= DN 25
	<= DN 25 (1”)
	Stainless steel
	Hastelloy®
	Stainless steel

with PTFE liner

	
> DN 25
	> DN 25 (1”)
	
	Hastelloy® stainless
	

	Float + Guide bracket
	Stainless steel
	Hastelloy®
	PTFE

	Display unit
	Aluminium (optional stainless steel) with safety glass pane


Operating conditions –all devices
	Temperature

	
	Type CF-S
	Type EF-H
	Type FF-P

	Max. Medium temp. TS
	-40 °C …+200 °C 
(opt. -80 °C …+350 °C)
	-20 °C …+125 °C

	Pressure

	
	Type CF-S
	Type EF-H
	Type FF-P

	Max. Medium pressure PS
	DN 15 – 

DN 150:
	PN 100 (optional up to 400 bar)
	PN 16

	
	½” – 6”:
	580 psi (optional up to 5800 psi)
	232 psi

	Min. operating pressure
	> 2 x pressure loss (see measuring ranges)

	Climate classification
	Weatherproof and/or non heated locations
Class C in accordance with DIN IEC 654 Section 1

	Protection class (DIN EN 60529)

	Display unit
	made of aluminium:
IP65

made of stainless steel:
IP66


Temperatures
	Device version
	Ambient temperature*
	Storage temperature

	
	[°C]
	[°F]
	[°C]
	[°F]

	without electrical components
	-40 …+80
	-40 …+176
	-40 …+80
	-40 …+176

	with limit switch(es)
	-40 …+65
	-40 …+149
	-40 …+65
	-40 …+149

	with 4 … 20 mA output
	-40 …+70
	-40 …+158
	-40 …+70
	-40 …+158

	 
	* 
IMPORTANT!

For applications in hazardous areas it is mandatory that the tempera​ture class of the type exami​nation certificate (protection type) will be regar​ded additionally.
For devices used in hazardous areas, additional safety notes apply; please refer to the Ex documentation!



RE250 with limit switch(es)
	Cable gland
	M20 x1.5

	Isolation (2 contacts)
	Galvanic isolated

	Terminal connection
	2.5 mm²

	Limit switch
	SJ3.5-N-BU

	Switching function
	NAMUR, NC

	Nominal voltage UO
	8.2 V DC (Ri approx. 1 kΩ)

	Supply voltage
	5 … 25 V DC


RE250 with current output 4 … 20 mA
	Cable gland
	M20 x1.5

	Terminal connection
	2.5 mm² 

	Auxiliary supply voltage UB
	14 V … 30 V DC

	Measuring signal
	4 … 20 mA = 0 … 100% flow value in 2-wire technology

	Power supply influence
	< 0.1 %

	Max. external load RB
	680 Ω (30 V)  
RB = (UB - 14V) / 22 mA

	Temperature influence
	< 10 µA / K


7.4
Dimensions and weights
Standard version (Housing of display made of aluminium)
[image: image23.jpg]169

Svy

90

L6

@1.D.

149

A

Y





	DN
	ANSI
	Ø I.D.
	A
	Weight

	15
	½”
	
26
(1,02)
	
74
(2,91)
	
3,0
(6,6)

	20
	¾”
	
26
(1,02)
	
74
(2,91)
	
3,0
(6,6)

	25
	1”
	
32
(1,26)
	
77
(3,03)
	
4,2
(9,3)

	32
	1 ¼”
	
32
(1,26)
	
77
(3,03)
	
5,2
(11,5)

	40
	1 ½”
	
46
(1,81)
	
88
(3,46)
	
6,0
(13,2)

	50
	2”
	
70
(2,76)
	
97
(3,82)
	
7,5
(16,5)

	65
	2 ½”
	
70
(2,76)
	
97
(3,82)
	
8,5
(18,7)

	80
	3”
	
102
(4,02)
	
113
(4,45)
	
13,0
(28,7)

	100
	4”
	
125
(4,92)
	
126
(4,96)
	
18,0
(39,7)

	125
	5”
	
125
(4,92)
	
126
(4,96)
	
22,0
(48,4)

	150
	6”
	
125
(4,92)
	
126
(4,96)
	
25,0
(55,0)


All Dimensions in mm (inch)
weights in kg (lbs)
Heating jacket version
[image: image24.jpg]A B 165~

A
Y
A
Y
A

149
L*
S
O

Y

44,5

—
=7

97

149 2I.D.

A
\

A
Y




	DN
	ANSI
	Ø I.D.
	A
	B
	S
	Weight

	15
	½”
	
26
(1,02)
	
74
(2,91)
	
110
(4,33)
	150

(5,91)
	
4,7
(10,4)

	20
	¾”
	
26
(1,02)
	
74
(2,91)
	
110
(4,33)
	150

(5,91)
	
4,7
(10,4)

	25
	1”
	
32
(1,26)
	
77
(3,03)
	
110
(4,33)
	150

(5,91)
	
5,9
(13,0)

	32
	1 ¼”
	
32
(1,26)
	
77
(3,03)
	
110
(4,33)
	150

(5,91)
	
6,9
(15,2)

	40
	1 ½”
	
46
(1,81)
	
88
(3,46)
	
130
(5,12)
	150

(5,91)
	
7,8
(17,2)

	50
	2”
	
70
(2,76)
	
97
(3,82)
	
140
(5,51)
	150

(5,91)
	
9,6
(21,1)

	65
	2 ½”
	
70
(2,76)
	
97
(3,82)
	
140
(5,51)
	150

(5,91)
	
11,0
(24,2)

	80
	3”
	
102
(4,02)
	
113
(4,45)
	
160
(6,30)
	150

(5,91)
	
16,0
(35,2)

	100
	4”
	
125
(4,92)
	
126
(4,96)
	
175
(6,89)
	
120
(4,72)
	
22,0
(48,4)

	125
	5”
	
125
(4,92)
	
126
(4,96)
	
175
(6,89)
	
120
(4,72)
	
26,0
(57,2)

	150
	6”
	
125
(4,92)
	
126
(4,96)
	
175
(6,89)
	
120
(4,72)
	
29,0
(63,8)


All Dimensions in mm (inch)
weights in kg (lbs)

* For dimension  L  please refer to page 33.

Stainless steel version
[image: image25.jpg]158™*

89

81

x|

961 J

0GZ

@d1.D.




	DN
	ANSI
	Ø I.D.
	A
	Weight

	15
	½”
	
26
(1,02)
	
103
(4,06)
	
3,1
(6,8)

	20
	¾”
	
26
(1,02)
	
103
(4,06)
	
3,1
(6,8)

	25
	1”
	
32
(1,26)
	
105
(4,13)
	
4,3
(9,5)

	32
	1 ¼”
	
32
(1,26)
	
105
(4,13)
	
5,3
(11,7)

	40
	1 ½”
	
46
(1,81)
	
115
(4,53)
	
6,1
(13,4)

	50
	2”
	
70
(2,76)
	
129
(5,08)
	
7,6
(16,7)

	65
	2 ½”
	
70
(2,76)
	
129
(5,08)
	
8,6
(18,9)

	80
	3”
	
102
(4,02)
	
145
(5,71)
	
13,1
(28,9)

	100
	4”
	
125
(4,92)
	
158
(6,22)
	
18,1
(39,9)

	125
	5”
	125
(4,92)
	
158
(6,22)
	
22,1
(48,6)

	150
	6”
	125
(4,92)
	
158
(6,22)
	
25,1
(55,2)


All Dimensions in mm (inch)
weights in kg (lbs)

* 
For dimension  L  please refer to page 33.
**
Dimension will be 258mm for version with displaced display unit

Mounting dimension L
[image: image26.jpg]



	Nom. Dia.
	EN
	Nom. 
Dia.
	ANSI

	
	PN 16
	PN 40
	PN 63
	PN 100
	
	150 lbs
	300 lbs
	600 lbs

	DN 15
	(
	250
	(
	250
	½”
	250
	250
	250

	DN 20
	(
	250
	(
	250
	¾”
	250
	250
	250

	DN 25
	(
	250
	(
	250
	1”
	250
	250
	250

	DN 32
	(
	250
	(
	250
	1 ¼”
	250
	250
	250

	DN 40
	(
	250
	(
	250
	1 ½”
	250
	250
	250

	DN 50
	(
	250
	250
	300
	2”
	250
	250
	300

	DN 65
	250
	250
	(
	(
	2 ½”
	250
	300
	300

	DN 80
	250
	250
	(
	(
	3”
	250
	300
	300

	DN 100
	250
	250
	(
	(
	4”
	250
	300
	300

	DN 125
	250
	300
	(
	(
	5”
	250
	300
	(

	DN 150
	250
	300
	(
	(
	6”
	250
	300
	(



All Dimensions in mm (inch)
( = not available
	Mecon GmbH

Röntgenstraße 105

D 50169 Kerpen

Tel.:
+49 (0)2237 600 06 – 0

Fax.:
+49 (0)2237 600 06 – 20

Email: 
customerservice@mecon.de
www.mecon.de
	[image: image27.jpg]TUVRheinland®

CERT

ISO 9001

A

-4 7
TUVRheinland

v o
2N







  RE 250  Variable Area Flowmeter





�


Fig 6.2	Replacing floats








1  Float


2  Upper guide bracket


3  Self-locking nut


4  Lower guide bracket





�


Fig 6.1	Replacing float damping 








1  Float with damping


2  Upper guide bracket


3  Self-locking nut


4  Lower guide bracket


5  Retaining clamp


6  Damping cylinder





1  Flowmeter RE250


2  Operating Instructions


3  Certificates (optional)


4  Software (optional)





1  Limit pointer


2  Fixing screw














© MECON GmbH 03/2011  OI_RE250_EN


