[image: image1.jpg]






[image: image5.wmf]Magnetic inductive transmitter

mag-flux

 M1

M

A

G

5

0

4

0

-

0

-

A

A

0

Power supply

• AC 230 V, 50/60 Hz

1

• AC 115 V, 50/60 Hz

2

• DC 18-36 V

3

Output / communication

• 4 - 20 mA

A

• 4 - 20 mA with HART protocol

B

Operator display and keypad

• without

A

• with

B

Cable glands

• M20/M16 x 1.5

1

• 1/2" - 14 NPT

2

Design

• remote version

1

• compact version

2

Other models

• Rating plate in English

B

1

1

• Measuring range, specify in plain text

Y

0

1

• Silicone-free materials

Y

0

4

• Measuring-point number

Y

1

5

• Measuring-point description

Y

1

6

• Stainless steel tag plate

Y

1

7




[image: image6.wmf]Magnetic inductive transmitter

mag-flux

 M1

M

A

G

5

0

4

0

-

0

-

A

A

0

Power supply

• AC 230 V, 50/60 Hz

1

• AC 115 V, 50/60 Hz

2

• DC 18-36 V

3

Output / communication

• 4 - 20 mA

A

• 4 - 20 mA with HART protocol

B

Operator display and keypad

• without

A

• with

B

Cable glands

• M20/M16 x 1.5

1

• 1/2" - 14 NPT

2

Design

• remote version

1

• compact version

2

Other models

• Rating plate in English

B

1

1

• Measuring range, specify in plain text

Y

0

1

• Silicone-free materials

Y

0

4

• Measuring-point number

Y

1

5

• Measuring-point description

Y

1

6

• Stainless steel tag plate

Y

1

7









[image: image7.jpg]MEC®N

FLOW-CONTROL-SYSTEMS




Fig 1
Magnetic inductive transmitter mag-flux M1(remote version)
__   Application domain

The mag-flux M1 is a microprocessor controlled and program​mable transmitter with pulsed constant field.

Measurement data from sensors of series mag-flux are processed by the transmitter. It is designed for flow velocities up to 10 m/s.

The device can be used to perform mea​sure​ments with any liquid with a minimum conductivity of 3 µS/cm, providing that the sensor’s material is suitable for the fluid.

The main applications for the mag-flux M1 are:

· Water and sewage plants

· Food and beverage industry

· Pulp and paper industry

__   Special features
· High-speed signal processing by 16-bit microcontroller
· Easy navigation with a two-line display (Option)
· Self-monitoring system
· Analog output (0/4-20 mA) and digital outputs (pulse, device status, limit, frequency)
· Internal simulation for all output values
· multilingual menus

__   System design

The complete metering system consists of a transmitter and a con​nected sensor e.g. mag-flux series with pulsed constant field.

The device mag-flux M1 can be installed directly on the sensor (com​pact version) or be mounted separately (remote version). The compact design applies to sensor types mag-flux A and mag-flux S (DN65 – DN100).

When using the transmitter with mag-flux S (DN15 – DN50), mag-flux F5 or probes mag-flux MIS 1/D and mag-flux MIS 2/15 only the remote version is available.

__   Operating principle
According to Faraday’s law of electromagnetic induction, an elec​trical voltage is generated by the sensor which is proportional to the velocity of the liquid inside the measuring tube.
This voltage is gained and processed by the mag-flux M1 and transduced into analog and digital outputs. 

A control unit is available as an additional option which provides a local display and the opportunity to customize the transmitter’s configuration.

The mag-flux M1 is prepared for HART® communication. An appropriate version is available on request. 

[image: image2.png]250 Q up to 600 Q

PC/ i
. Coupling
Laptop [ j © ol module -
= HART-

/@% @\ RS-232-C Communicator





Fig 2
Electrical connection for HART® communication, schematic diagram

____________________________________________________________

__   Application note
· The magnetic-inductive metering system is entirely suitable for the measurement of volume flow rates of conductive liquids.
· Before replacing a compact version of the mag-flux M1 ensure that the meter is pressureless and free from hazardous media.

· The operation of the device is only valid within the tempe​ra​ture range specified on the rating plate.

· The limits for the electrical connections of the transmitter are specified on the rating plate and have to be observed strictly.

· The transmitter is compliant with the EMC Directive 89/336/EEC und low-voltage Directive 73/23/EWG. 

· The mag-flux M1 is designed for mainly stationary appli​ca​tions.

· Improper installation and use of the transmitter (metering  sys​tem) could cause a loss of warranty.




__   Technical Data
	Mode of operation and design 
	

	Measuring principle
	magnetic inductive with pulsed constant field (PDC)

	Magnetic field excitation
	Internal clock with DC supply

	
	1,56 Hz / 3,125 Hz / 6,25 Hz /

12,5 Hz / 25 Hz

	Outputs
	

	Electrical isolation
	outputs electrically isolated from each other and from the power supply

	Current output
	

	· Signal
	

	- Signal range
	0 ... 20 mA / 4 ... 20 mA, selectable

	- Failure signal
	> 22 mA oder < 3,8 mA, can be switched

	· Load
	

	- Output
	< 600 Ω

	- for HART communication
	≥ 250 Ω

	Communication
	via analog output with PC coupling module or HART Communicator

	· Protocol
	HART, version 7.0

	Digital output
	

	· Signal 
	

	- Design
	Optocoupler, passive

	- Rated values
	max. 1,8W, max. 30 V, 60 mA

	Output configuration
	

	· Pulse
	

	- Significance
	≤ 1000 pulses/s

	- Pulse width
	≥ 0,1 ms (max. 2s), selectable

	· Frequency
	

	- Signal range
	0 ... 1 kHz

	Digital output 2
	

	· Signal 
	

	- Design
	Optocoupler, passive



	- Rated values
	max. 1,8W, max. 30 V, 60 mA



	· Output configuration
	Status output: forward flow, reverse Flow, MIN, MAX, Alarm (selectable)

	Measuring accuracy (under reference conditions)

	Pulse output


	Basic accuracy: refer to datasheet of the connected sensor

±0,05 % per 10 K

	Current output


	Basic accuracy: refer to datasheet of the connected sensor

±0,1 % per 10 K

	Reproducibility
	refer to datasheet of the connected sensor




	Operating conditions
	

	Installation conditions
	See also datasheet of the connected sensor 

	Ambient temperature
	

	· Remote version
	-20 ... +60 °C (-4 ... +140 °F)

	· Compact version
	-20 ... +60 °C (-4 ... +140 °F)

Processtemp.: max. 60 °C (104 °F)

	· Control unit
	0 ... +50 °C (32 ... 122 °F)

	Storage
	-25 ... +80 °C (-13 ... +176 °F)

	Degree of protection
	IP 67 / NEMA 4X

	Electromagnetic compatibility (EMC)

	· Emitted interference
	acc.  to EN 61000-6-3:2001 
(for use in home and industry)

	· Noise immunity
	acc. to EN 61000-6-2:1999 
(for use in industry)

NAMUR NE21 (Ver. 10.02.2004)

	Construction
	

	Weight
	2,4 kg (5,3 lb)

	Compact version
	Transmitter permanently mounted on measuring tube

	Remote version
	Transmitter connected to the sensor by a shielded cable

	Maximum line length
	200 m (656 ft)*

*Line length depends on the conductivity of the media

	Housing
	die-cast aluminium, painted

	Control unit (Option)
	

	General display
	LCD, background illumination

two rows of 16 characters

	Multi-display for
	flow, volume, flow velocity

	Key pad
	6 keys for input

	Power supply
	as specified on the rating plate

	· AC voltage
	230 V, ±10 %, 50/60 Hz

115 V. ±10 %, 50/60 Hz

	· DC voltage
	24 V, ±15 %

	· Power consumption
	approx. 10 VA

	· Mains fuse
	

	- AC voltage
	100 mA (T)

	- DC voltage
	1 A (T)


__   Dimensions

[image: image3.jpg]A

A

A

217

195

A 4

Y

A

125

Y

Y





[image: image4.jpg]184

109

08

A
A A

\
&
N

o

93

149

A

G

\ 4







__   Order code









� EMBED Excel.Sheet.8  ���





















































	
	
	
	
	

	Mecon GmbH
	Phone +49(0)2237 600 06 - 0
	
	Fax +49(0)2237 600 06 – 40
	page 2 of 3

	Röntgenstraße 105
	www.mecon.de
	
	customerservice@mecon.de
	Mecon 03/2010

	D-50169 Kerpen
	
	
	
	


	
	
	
	
	

	Mecon GmbH
	Phone +49(0)2237 600 06 - 0
	
	Fax +49(0)2237 600 06 - 40
	page 3 of 3

	Röntgenstraße 105
	www.mecon.de
	
	customerservice@mecon.de
	Mecon 03/2010

	D-50169 Kerpen
	
	
	
	



_1332319664.xls
Gum

		Magnetic inductive transmitter

		mag-flux M1

								M		A		G		5		0		4		0		-										0		-				A		A		0

		Power supply

		• AC 230 V, 50/60 Hz																						1

		• AC 115 V, 50/60 Hz																						2

		• DC 18-36 V																						3

		Output / communication

		• 4 - 20 mA																								A

		• 4 - 20 mA with HART protocol																								B

		Operator display and keypad

		• without																										A

		• with																										B

		Cable glands

		• M20/M16 x 1.5																												1

		• 1/2" - 14 NPT																												2

		Design

		• remote version																																		1

		• compact version																																		2

		Other models

		• Rating plate in English																												B		1		1

		• Measuring range, specify in plain text																												Y		0		1

		• Silicone-free materials																												Y		0		4

		• Measuring-point number																												Y		1		5

		• Measuring-point description																												Y		1		6

		• Stainless steel tag plate																												Y		1		7






